## Policy Search
Policy | Description | Geography | Products Type | Policy Approach | Policy Instrument | Policy Status | Adopted | Revised | Updated by CLASP | Fuel Types | Test Method Applied | Responsible Agency | Related Topics | Permalink | Source
Energy Conservation (Regulated Goods and Registered Suppliers) Regulations 2017 | This regulation specifies the MEPS and labeling requirements for air‑conditioners; single-phase clothes dryers; single-phase lamps; ballasts for fluorescent lamps; single-phase refrigerators without freezers, refrigerators with freezers, and refrigerators with freezers and through-the-door ice dispensers; single‑phase televisions; and single speed three-phase 50 Hz induction motors. | Singapore* | Televisions, Clothes Dryers, Non-Directional lamps, Directional Lamps, Fluorescent and HID Lighting, 3-Phase Motors, Room ACs - Stationary ACs, Refrigerators-Freezers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised |  |  | October 2022 | Electricity | Single-phase non-ducted room air conditioners: ISO 5151:2017, ISO 15042:2017 , Refrigerators: ISO 15502:2005; IEC 62552:2007 , Clothes Dryers: IEC 61121:2005 , Televisions: IEC 62087:2008 , General Lighting: CIE 84:1989; IEC 60064 , Three-phase VRF air-conditioners: ISO 15042:2017 , Three-phase induction motors: IEC 60032:2014 | Minister for the Environment and Water Resources | Energy Efficiency | https://cprc-clasp.ngo/policies/energy-conservation-regulated-goods-and-registered-suppliers-regulations-2017 | https://sso.agc.gov.sg/Act/ECA2012/Uncommenced/20171227?ValidDt=20180101&ViewType=Sl
JS 2091:2013 Technical Regulation on eco-design - Requirements for non-directional household lamps | This policy establishes eco-design requirements for the placing on the market of non-directional household lamps, including when they are marketed for non-household use or when they are integrated into other products. It also establishes product information requirements for special purpose lamps. | Jordan | Non-Directional lamps | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2092 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20912013-technical-regulation-eco-design-requirements-non-directional-household-lamps | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5461
JS 2092:2013 Energy efficiency labeling of household electric lamps | This policy covers household electric lamps supplied directly from the mains (filament and integral compact fluorescent lamps), and to household fluorescent lamps (including linear, and non-integral compact fluorescent lamps), even when marketed for non-household use. | Jordan | Tubular Lamps, Non-Directional lamps | Mandatory | Comparative Label | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2092 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20922013-energy-efficiency-labeling-household-electric-lamps | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5453
JS 2093:2013 Technical regulation on eco-design requirements for fluorescent lamps without integrated ballast; for high intensity discharge lamps; and for ballasts and luminaires able to operate such lamps | This policy establishes ecodesign requirements for the placing on the market of fluorescent lamps without integrated ballast, of high intensity discharge lamps, and of ballasts and luminaires able to operate such lamps as defined in Article 3, even when they are integrated into other energy related products. | Jordan | Tubular Lamps, Drivers/ Controls | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2092 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20932013-technical-regulation-eco-design-requirements-fluorescent-lamps-without | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5462
JS 2094:2013 Technical Regulation on eco-design requirements for electric motors | This policy establishes ecodesign requirements for placing on the market and for putting into service of motors, including where integrated in other products. | Jordan | 3-Phase Motors | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2094 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20942013-technical-regulation-eco-design-requirements-electric-motors | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5463
JS 2095:2013 Technical regulation on eco-design requirements for Glandless standalone circulators and glandless circulators integrated in products | This policy establishes ecodesign requirements for placing on the market of glandless standalone circulators and glandless circulators integrated in products. | Jordan | Building Circulator Pumps | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2095 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20952013-technical-regulation-eco-design-requirements-glandless-standalone-circulators | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5464
JS 2097:2013 Energy labeling of household combined washer-driers | This policy covers electric mains operated household combined washer-driers. Appliances that can also use other energy sources are excluded. | Jordan | Washer and Dryers | Mandatory | Comparative Label | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity, Water | JS 2096 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20972013-energy-labeling-household-combined-washer-driers | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5458
JS 2098:2013 Energy labeling of household electric ovens | This policy covers electric mains operated household electric ovens including ovens being part of larger appliances. | Jordan | Ovens | Mandatory | Comparative Label | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2098 | National Energy Research Centre (NERC) | Cookstoves, Energy Efficiency | https://cprc-clasp.ngo/policies/js-20982013-energy-labeling-household-electric-ovens | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5454
JS 2099:2013 Technical Regulation on eco-design requirements for household dishwashers | This policy establishes ecodesign requirements for placing on the market of electric mains-operated household dishwashers and electric mains-operated household dishwashers that can also be powered by batteries, including those sold for non-household use and built-in household dishwashers. | Jordan | Dishwashers | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity, Water | JS 2099 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-20992013-technical-regulation-eco-design-requirements-household-dishwashers | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5465
JS 2100:2013 Energy labeling of household dishwashers | This policy covers electric mains-operated household dishwashers and electric mains-operated dishwashers that can also be powered by batteries; including those sold for non-household use and built-in household dishwashers. | Jordan | Dishwashers | Mandatory | Comparative Label | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity, Water | JS 2100 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21002013-energy-labeling-household-dishwashers | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5452
JS 2101:2013 Energy labeling for household refrigerating appliances | This policy covers the labeling of and provision of supplementary product information on electric mains-operated household refrigerating appliances with a storage volume between 10 and 1,500 litres. | Jordan | Refrigerators-Freezers, Freezers-only | Mandatory | Comparative Label | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 1749 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21012013-energy-labeling-household-refrigerating-appliances | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5455
JS 2102:2013 Technical Regulation on eco-design requirements for household refrigerating appliances | This policy establishes ecodesign requirements for placing on the market of electric mains-operated household refrigerating appliances with a storage volume up to 1500 litres. | Jordan | Refrigerators-Freezers, Freezers-only | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 1749 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21022013-technical-regulation-eco-design-requirements-household-refrigerating | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5466
JS 2105:2013 Energy labeling of televisions | This policy covers labelling and the provision of supplementary product information for televisions. | Jordan | Televisions, Displays | Mandatory | Comparative Label | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2105 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21052013-energy-labeling-televisions | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5456
JS 2106:2013 Technical Regulation on eco-design requirements for televisions | This policy establishes ecodesign requirements for placing on the market of televisions. | Jordan | Televisions, Displays | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2106 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21062013-technical-regulation-eco-design-requirements-televisions | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5468
JS 2107:2013 Technical Regulation on eco-design requirements for air conditioners and comfort fans | This policy establishes ecodesign requirements for the placing on the market of electric mains-operated air conditioners with a rated capacity of 12 kW for cooling, or heating if the product has no cooling function, and comfort fans with an electric fan power input of 125W. | Jordan | Portable Fans, Room ACs - Stationary ACs, Portable ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2107 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21072013-technical-regulation-eco-design-requirements-air-conditioners-and-comfort-fans
JS 2108:2013 Energy efficiency labeling of air conditioners | This policy establishes requirements for the labelling and the provision of supplementary product information for electric mains-operated air conditioners with a rated capacity of 12 kW for cooling or heating if the product has no cooling function. This policy does not apply to: a) appliances that use non-electric energy sources; b) air conditioners of which the condensor- or evaporator-side do not use air for heat transfer medium. | Jordan | Room ACs - Stationary ACs | Mandatory | Comparative Label | Entered into force, Revised | 2012 | 2013 | June 2021 | Electricity | JS 2107 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21082013-energy-efficiency-labeling-air-conditioners | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5451
JS 2110:2013 Technical Regulation on eco-design requirements for simple set-top boxes | This policy establishes ecodesign requirements for simple set-top boxes. | Jordan | Set Top Boxes (STB) | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2110 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21102013-technical-regulation-eco-design-requirements-simple-set-top-boxes | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5470
JS 2111:2013 Technical Regulation on eco-design requirements for no-load condition electric power consumption and average active efficiency of external power supplies | This policy establishes ecodesign requirements related to electric power consumption in no-load condition and average active efficiency of external power supplies. | Jordan | External Power Supply | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2092 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21112013-technical-regulation-eco-design-requirements-no-load-condition-electric-power | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5471
JS 2112:2013 Technical Regulation on eco-design requirements for fans | This policy establishes ecodesign requirements for the placing on the market or putting into service of fans, including those integrated in other energy-related products as covered by the Framework Technical Regulation. | Jordan | Integrated Fans | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2013 | 2014 | June 2021 | Electricity | JS 2112 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-21122013-technical-regulation-eco-design-requirements-fans | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5472
JS 50564:2012 Electrical and electronic household and office equipment - Measurement of low power consumption | This policy specifies methods of measurement of electrical power consumption and the reporting of the results for a range of electrical and electronic household and office equipment, hereafter referred to as products. | Jordan | Stand-by and networked devices | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2012 | 2013 | June 2021 | Electricity | JS 62301 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-505642012-electrical-and-electronic-household-and-office-equipment-measurement-low | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5279
JS 60456:2012 Clothes washing machines for household use - Methods for measuring the performance (EN 60456:2001 + AC:2011) | This policy specifies methods for measuring the performance of clothes washing machines for household use, with or without heating devices utilising cold and/or hot water supply. It also deals with appliances for water extraction by centrifugal force (spin extractors) and is applicable to appliances for both washing and drying textiles (washer-dryers). | Jordan | Washer and Dryers | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2012 | 2013 | June 2021 | Electricity, Water | JS 2103 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-604562012-clothes-washing-machines-household-use-methods-measuring-performance-en | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5305
JS 61121:2012 Tumble dryers for household use - Methods for measuring the performance | This policy covers household electric tumble dryers of the automatic and non-automatic type, with or without a cold water supply and incorporating a heating device. | Jordan | Clothes Dryers | Mandatory | Comparative Label | Entered into force, Revised | 2012 | 2013 | June 2021 | Electricity | JS 2096 | National Energy Research Centre (NERC) | Energy Efficiency | https://cprc-clasp.ngo/policies/js-611212012-tumble-dryers-household-use-methods-measuring-performance | http://www.jsmo.gov.jo/en/EServices/Standards/Pages/stdDetails.aspx?mfn=5293
MELS for Casement and Window Air-Conditioners | This policy defines the minimum energy labeling scheme for casement and window air-conditioners up to 8.8kW. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | New | 2008 | 2014 | December 2023 | Electricity | ISO 5151:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Clothes Dryers | This policy defines minimum energy labeling scheme (MELS) requirements for clothes dryers with a rated capacity of up to 10kg. Energy Consumption (EC) per wash in kWh (all clothes dryers) - 1 tick: NA - 2 tick: Rated capacity x 0.55 ≥ EC > Rated capacity x 0.45 - 3 tick: Rated capacity x 0.45 ≥ EC > Rated capacity x 0.37 - 4 tick: Rated capacity x 0.37 ≥ EC > Rated capacity x 0.30 - 5 tick: Rated capacity x 0.30 ≥ EC Rated Capacity means the mass in kilograms of a particular type of dry textiles which, according to the instructions of the manufacturer of the clothes dryer, can be treated in a particular drying program suitable for drying the particular type of dry textile. | Singapore* | Clothes Dryers | Mandatory | Comparative Label | Revised | 2009 | 2014 | December 2023 | Electricity | IEC 61121:2005 with amendment 1 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-clothes-dryers | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Commercial Storage Refrigerators (2025) | This policy defines minimum energy labeling scheme requirements for chiller, freezers, and combinations type of all capacities. | Singapore* | Refrigerated Cabinets, Wine Chillers, Walk-In Coolers and Freezers, Refrigerated Vending Machines, Freezers-only | Mandatory | Comparative Label | Entered into force, New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-commercial-storage-refrigerators-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for General Lighting (2019) | This policy defines minimum energy labeling scheme requirements for incandescent lamps, CFLi lamps, and LEDs with an Edison screw or a bayonet lamp cap. | Singapore* | Tubular Lamps, Non-Directional lamps | Mandatory | Comparative Label | Revised, Superseded | 2015 | 2019 | December 2023 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-general-lighting-2019 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for General Lighting (2024) | This policy set energy label scheme for all regulated lamps: | Singapore* | Tubular Lamps, Non-Directional lamps | Mandatory | Comparative Label | Entered into force, Revised | 2015 | 2024 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-general-lighting-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Portable Air-Conditioners (2024) | This policy defines the minimum energy labeling scheme for single-phase portable air-conditioners: | Singapore* | Portable ACs | Mandatory | Comparative Label | Entered into force, New |  | 2024 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-portable-air-conditioners-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Refrigerators | This policy defines minimum energy labeling scheme requirements for the following products: - Refrigerators without a freezer up to 900L - Refrigerators with a freezer up to 300L - Refrigerators with a freezer > 300L to 900L - Refrigerators with freezer and through-the-door ice dispenser | Singapore* | Refrigerators-Freezers | Mandatory | Comparative Label | New | 2008 | 2014 | December 2023 | Electricity | IEC 62552:2007 , ISO 15502:2005 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-refrigerators | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Split Type Air-Conditioners | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | Revised | 2008 | 2014 | December 2023 | Electricity | ISO 15042:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-split-type-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Televisions | This policy contains minimum energy labeling scheme (MELS) requirements for televisions. | Singapore* | Televisions | Mandatory | Comparative Label | New | 2014 |  | December 2023 | Electricity | IEC 62087:2008 , IEC 62087:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-televisions | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Three-Phase VRF Air-Conditioners | This policy defines the minimum energy labeling scheme requirements for base module/units of a three-phase VRF air-conditioners (unit efficiency) of all cooling capacities. | Singapore* | Central ACs | Mandatory | Comparative Label | New | 2021 |  | December 2023 | Electricity | ISO 15042:2017 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-three-phase-vrf-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Water Heater (2025) | This policy defines minimum energy labeling scheme requirements for all regulated water heaters: | Singapore* | Instantaneous Water Heaters, Storage Water Heaters | Mandatory | Comparative Label | New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-water-heater-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MEPS for casement and window air-conditioners | This policy applies to casement and window (up to 8.8 kW). The Minimum Coefficient of Performance (COP) is set at COP100% > 3.78. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards: ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2022 | December 2023 | Electricity | ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Clothes Dryers | This policy defines minimum energy performance requirements for clothes dryers with a rated capacity of https://www.nea.gov.sg/up to 10kg. The revised 2022 MEPS are: EC ≤ [Rated Capacity x 0.55], where “Rated Capacity” means the mass in kilograms of a particular type of dry textiles which, according to the instructions of the manufacturer of the clothes dryer, can be treated in a particular drying program suitable for drying the particular type of dry textile and “EC” means Energy Consumption in kWh per wash. | Singapore* | Clothes Dryers | Mandatory | Minimum Performance Standard | Revised | 2014 | 2022 | December 2023 | Electricity | IEC1 61121:2005 with amendment 1, Section 9.2.1: Drying tests general | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-clothes-dryers | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Commercial Storage Refrigerators (2025) | This policy sets minimum energy performance standards for commercial storage refrigerators as shown below | Singapore* | Refrigerated Cabinets, Wine Chillers, Walk-In Coolers and Freezers, Refrigerated Vending Machines, Freezers-only | Mandatory | Minimum Performance Standard | Entered into force, New | 2025 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-commercial-storage-refrigerators-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for General Lighting | This policy sets minimum energy performance requirements for the following products: incandescent lamps (25-200W), Compact fluorescent lamps with integrated ballast (CFLi) (up to 60W), LED lamps with an Edison screw or a bayonet lamp cap (up to 60W), Compact fluorescent lamps without integrated ballast (CFLni), T8 Linear, double-capped, fluorescent lamps (LFL)[0.5 - 1.5]m, and LED lamps designed as a direct replacement for CFLni and T8 LFL without requiring any internal modification of the luminaires. | Singapore* | Lighting, Lamps, Tubular Lamps, Non-Directional lamps, HD lamps and retrofits | Mandatory | Minimum Performance Standard | Revised, Superseded | 2015 | 2019 | December 2023 | Electricity | CIE3 84:1989 and IEC 60064, Measurement of luminous flux , CIE 84:1989 and IEC 60064 or IEC 60357, Measurement of luminous flux , IEC 60969:2001, Performance tests , IEC 60901:2001, Performance tests , IEC 60081:2002, Performance tests , IEC 62612:2013, Performance tests , IEC 62612:2013, Performance tests | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-general-lighting | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for General Lighting (2024) | This policy sets minimum energy performance standards for lamps as shown below | Singapore* | Tubular Lamps, Non-Directional lamps | Mandatory | Minimum Performance Standard | Revised | 2015 | 2024 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-general-lighting-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Portable Air-Conditioners (2024) | This policy regulates minimum energy performance standard for portable air conditioners. Single-phase portable air-conditioners having a single exhaust duct (up to 12 kW) should have Coefficient of Performance (COP) 100% equal or greater than 3.0. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards. 1 Weighted COP = 0.4 x COP100% + 0.6 x COP50% N is the number of indoor and outdoor units Standby power is expressed in Watts | Singapore* | Portable ACs | Mandatory | Minimum Performance Standard | New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-portable-air-conditioners-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Refrigerators (2022) | This policy defines minimum energy performance requirements for the following refrigerators: - Refrigerators without a freezer up to 900L: - Refrigerators with a freezer up to 300L: AEC ≤ [(465 + 1.378 xVadj tot) x 0.427] - Refrigerators with a freezer > 300L to 900L: AEC ≤ [(465 + 1.378 xVadj tot) x 0.427] - Refrigerators with freezer and through-the-door ice dispenser: AEC ≤ [(585 + 1.378 x Vadj tot) x 0.409] - Vadj tot is defined as the sum of the adjusted volumes of the refrigerator compartments. - “Through-the-door ice dispenser” means an automatic ice maker coupled with a device that delivers ice on demand externally through a door. - “AEC” means Annual Energy Consumption. | Singapore* | Refrigerators-Freezers | Mandatory | Minimum Performance Standard | Revised, Superseded | 2011 | 2022 | December 2023 | Electricity | IEC 62552:2007 or ISO2 15502:2005, Section 15: Energy consumption test, climate class T | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-refrigerators-2022 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Refrigerators (2025) | This policy raises minimum energy performance standards for refrigerators with adjusted volumes no greater than 900 litres. | Singapore* | Refrigerators-Freezers | Mandatory | Minimum Performance Standard | Revised | 2011 | 2025 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-refrigerators-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners (2022) | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. The established MEPS are: Single/Multi Split (inverter) up to 17.6kW: COP100% ≥ 3.34 Single/Multi Split (inverter) up to 17.6kW: COPweighted ≥ 4.04 Single/Multi Split (non-inverter) up to 17.6kW: COP100% ≥ 4.04 COPweighted = 0.4 x COP100% + 0.6 x COP50% | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Revised, Superseded | 2011 | 2022 | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , ISO 5151:2017, Section 5.1: Cooling capacity test, Climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011, Climate class Nil | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-split-type-air-conditioners-2022 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners (2025) | This policy raises MEPS for single and multi split air conditioners. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2025 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-split-type-air-conditioners-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Televisions (2024/2025) | This policy sets minimum energy performance standards for non-8K TV at 4-tick and 8K TV at 3-tick, effective in April 2024, and April 2025 respectively, as shown below | Singapore* | Televisions | Mandatory | Minimum Performance Standard | Entered into force, New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-televisions-20242025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Three-Phase Induction Motors (2018) | This policy applies to three-phase induction motors with a rated output from 0.75kW to 200kW and three-phase induction motors with a rated output >200kW to ≤ 375kW. | Singapore* | 3-Phase Motors | Mandatory | Minimum Performance Standard | New | 2018 |  | December 2023 | Electricity | IEC 60034-2-1 (2014), Method 2-1-1B , IEEE 112 (2004), Method B | National Environment Agency | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/policies/meps-three-phase-induction-motors-2018 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Three-Phase VRF Air-Conditioners (2021) | A base module/unit of a three-phase VRF air-conditioner (unit efficiency) of all cooling capacities must meet the following Minimum Integrated Energy Efficiency Ratio (IEER): ≥ 4.35. Integrated Energy Efficiency Ratio (IEER) = (0.020 x A) + (0.617 x B) + (0.238 x C) + (0.125 x D) where A = COP at full load cooling capacity tested under ISO 15042 T1 condition, B = COP at 75% part load cooling capacity tested under ISO 15042 T1 condition, C = COP at 50% part load cooling capacity tested under ISO 15042 T1 condition, D = COP at 25% part load cooling capacity tested under ISO 15042 T1 condition. | Singapore* | Central ACs | Mandatory | Minimum Performance Standard | New | 2021 |  | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-three-phase-vrf-air-conditioners-2021 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Water Heater (2025) | This policy sets minimum energy performance standards for water heaters as shown below | Singapore* | Instantaneous Water Heaters, Storage Water Heaters | Mandatory | Minimum Performance Standard | Entered into force, New | 2025 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-water-heater-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
RTS 23.01.01:15 Energy efficiency. Central, packaged, split air conditioners. Limits, test methods and labelling requirements | This standard specifies the MEPS (in SEER) and labeling requirements for central, packaged, and split air conditioners, operated with electric power with frequency of 60 Hz and having cooling capacities from 8,800W to 19,050W. It does not apply to inverters. | El Salvador | Room ACs - Stationary ACs, Central ACs | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2019 |  | October 2019 | Electricity |  | National Energy Council | Energy Efficiency | https://cprc-clasp.ngo/policies/rts-23010115-energy-efficiency-central-packaged-split-air-conditioners-limits-test-methods | http://www.osartec.gob.sv/index.php?option=com_jdownloads&Itemid=0&view=finish&cid=1398&catid=4
RTS 23.01.02:15 Energy efficiency. Room air-conditioners. Limits, test methods and labelling requirements | This standard specifies the MEPS (in SEER) and labeling requirements for room air conditioners, with or without a heat pump, with air-cooled condensers and cooling capacities of up to 10,600W. | El Salvador | Room ACs - Stationary ACs | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2019 |  | October 2019 | Electricity |  | National Energy Council | Energy Efficiency | https://cprc-clasp.ngo/policies/rts-23010215-energy-efficiency-room-air-conditioners-limits-test-methods-and-labelling | http://www.osartec.gob.sv/index.php?option=com_jdownloads&Itemid=0&view=finish&cid=1400&catid=4
RTS 23.01.03:15 Energy efficiency. Split, free-flow, ductless air-conditioners. Limits, test methods and labelling requirements | This standard specifies the MEPS (in SEER) and labeling requirements for split, free-flow, ductless air-conditioners (known as mini-split and multi-split air-conditioners), whether single-cycle (cooling only) or reverse-cycle (heat pump), with air-cooled condensers. | El Salvador | Room ACs - Stationary ACs | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2019 |  | October 2019 | Electricity |  | National Energy Council | Energy Efficiency | https://cprc-clasp.ngo/policies/rts-23010315-energy-efficiency-split-free-flow-ductless-air-conditioners-limits-test | http://www.osartec.gob.sv/index.php?option=com_jdownloads&Itemid=0&view=finish&cid=1397&catid=4
RTS 97.01.01:15 Energy efficiency. Household refrigerators and freezers. Limits, test methods and labelling requirements | This standard specifies the MEPS and labeling requirements for household refrigerators, refrigerators-freezers | El Salvador | Refrigerators-Freezers, Freezers-only | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2019 |  | October 2019 | Electricity |  | National Energy Council | Energy Efficiency | https://cprc-clasp.ngo/policies/rts-97010115-energy-efficiency-household-refrigerators-and-freezers-limits-test-methods | http://www.osartec.gob.sv/index.php?option=com_jdownloads&Itemid=0&view=finish&cid=1395&catid=4
RTS 97.02.01:15 Energy efficiency. Self-contained commericial refrigeration equipment. Limits, test methods and labelling requirements | This standard specifies the MEPS and labeling requirements for commercial self-contained refrigeration appliances (freezers, coolers, display cabinets, ice bag conservators). | El Salvador | Refrigerated Cabinets, Freezers-only | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2019 |  | October 2019 | Electricity |  | National Energy Council | Energy Efficiency | https://cprc-clasp.ngo/policies/rts-97020115-energy-efficiency-self-contained-commericial-refrigeration-equipment-limits | http://www.osartec.gob.sv/index.php?option=com_jdownloads&Itemid=0&view=finish&cid=1396&catid=4
RTS 29.01.01:15: Energy efficiency. Three-phase squirrel-cage AC induction motors with a rated output of 0.746 to 373 kW. Limits, test methods and labelling requirements | This standard specifies the MEPS and labeling requirements for open- and closed-loop three-phase squirrel-cage electric AC induction motors with a rated output of 0.746 kW to 373 kW. | El Salvador | 3-Phase Motors | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2019 |  | October 2019 | Electricity |  | National Energy Council | Energy Efficiency | https://cprc-clasp.ngo/policies/rts-29010115-energy-efficiency-three-phase-squirrel-cage-ac-induction-motors-rated-output | https://osartec.gob.sv/?p=5614
Singapore Green Labeling Scheme: CFLs | This standard establishes requirements for integral compact fluorescent lamps (CFL) where the tube and ballast are combined into a single unit. These lamps allow consumers to replace incandescent lamps easily with CFL. The product group that is within the scope of certification would include screw-based lamps with ballast and adaptor in a single assembly. | Singapore* | Non-Directional lamps, Directional Lamps | Voluntary | Endorsement Label | Entered into force, New | 2012 |  | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labeling-scheme-cfls | https://www.sgls.sec.org.sg/categoryinfo.php?cid=7
Singapore Green Labeling Scheme: Hand Dryers | This policy establishes criteria for electric hot air hand driers that are equipped with non-contact on-off switches based on environmental, performance, and health parameters. | Singapore* | Other | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labeling-scheme-hand-dryers | https://www.sgls.sec.org.sg/categoryinfo.php?cid=49
Singapore Green Labeling Scheme: Microwave Ovens | This policy establishes criteria for microwave ovens for household use. A microwave oven is an electrical appliance intended for household use that uses high-frequency electromagnetic waves for heating food or beverages, with a rated voltage of not more than 250 V and a frequency ranging from 890 MHz to 6 GHz. | Singapore* | Microwaves | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labeling-scheme-microwave-ovens | https://www.sgls.sec.org.sg/categoryinfo.php?cid=81
Singapore Green Labeling Scheme: Personal Computers | This policy establishes criteria to label Personal Computers (PCs). These criteria include requirements for the following with a rated voltage of not more than 250 VAC: computer system unit; display (monitor); personal computer set combination system including units Computer System Unit, display (monitor), keyboard, and mouse; and portable computer such as notebook (notebook or laptop), tablet (tablet or slate). | Singapore* | Information Technology | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labeling-scheme-personal-computers | https://www.sgls.sec.org.sg/categoryinfo.php?cid=82
Singapore Green Labeling Scheme: Photocopiers, Printers, Fax Machines & Multifunctional Devices | This policy establishes grading criteria for Copying Machines, Printers, Fax Machines, and Multifunctional Devices (MFDs) based on environmental, performance, and health parameters. These criteria include requirements for standard-sized monochromatic and color office machines based on electrophotography (including laser and LED) and inkjet marking technologies. Standard-sized machines are those that primarily print or copy on regular-sized (e.g., A4 / 8.5 x 11) paper and envelopes. Large-format office machines are also included in this category. | Singapore* | Other-Electronics | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labeling-scheme-photocopiers-printers-fax-machines-multifunctional-devices | https://www.sgls.sec.org.sg/categoryinfo.php?cid=38
Singapore Green Labeling Scheme: Televisions Sets | This category establishes criteria for mains-powered television sets consisting of a unit whose main purpose is to receive, reproduce and, if applicable, decode television signals. | Singapore* | Televisions | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labeling-scheme-televisions-sets | https://www.sgls.sec.org.sg/
Singapore Green Labelling Scheme: Coffee Machine | This category establishes criteria for espresso and coffee machines, which include fully-automatic espresso/coffee machines, hand-operated piston espresso/coffee machines and capsule espresso/coffee machines. The category does not cover espresso/coffee machines with a system to warm cups, or capsule espresso/coffee machines which require capsules made by a certain manufacturer. | Singapore* | Coffee Machines | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-coffee-machine | https://www.sgls.sec.org.sg/categoryinfo.php?cid=56
Singapore Green Labelling Scheme: Dishwashers | This category establishes criteria for dishwashers designed to be stand-alone on floors or counter surfaces meant for household use. They apply to devices which serve the function of dishwashing alone or in combination with other functions. | Singapore* | Dishwashers | Voluntary | Endorsement Label | Entered into force, New | 2013 |  | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-dishwashers | https://www.sgls.sec.org.sg/categoryinfo.php?cid=76
Singapore Green Labelling Scheme: Electric Kettles | This category establishes criteria for electric kettles for household use based on environmental, performance and health parameters. | Singapore* | Electric Kettles | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-electric-kettles | https://www.sgls.sec.org.sg/categoryinfo.php?cid=55
Singapore Green Labelling Scheme: Gas Cookers and Gas-fired Appliances | This category establishes criteria for household gas-powered cooking devices that are isolated in design i.e. individual machines (which operate with gas burners located on steel originated or glass and ceramic layered cooker top) and gas-powered cooking devices with built-in ovens (the latter may be either natural gas or electricity powered). This category does not include gas powered cooking devices which operate with gas burners located below a glass and ceramic layered cooker top. | Singapore* | Cooktops or Hobs | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Gas |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-gas-cookers-and-gas-fired-appliances | https://www.sgls.sec.org.sg/categoryinfo.php?cid=57
Singapore Green Labelling Scheme: Hot Water Storage Tanks | This scope for certification under this category includes hot-water storage tanks such as thermal solar systems and components, including water heaters, water heating installations, and storage water heaters for drinking water. | Singapore* | Storage Water Heaters | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Electricity, Solar |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-hot-water-storage-tanks | https://www.sgls.sec.org.sg/categoryinfo.php?cid=58
Singapore Green Labelling Scheme: LEDs | This category establishes criteria for a range of Light Emitting Diode (“LED lighting”), which is used by directly connecting to a commercial power source. | Singapore* | Streetlighting, Non-Directional lamps, Directional Lamps | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2017 | November 2020 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-leds | https://www.sgls.sec.org.sg/categoryinfo.php?cid=45
Singapore Green Labelling Scheme: Photovoltaic Equipment | This category establishes criteria for products for indoor and outdoor use, powered by solar (or light) energy using a rechargeable electrochemical storage system are included within the scope of this category based on environmental, performance, and health parameters. | Singapore* | Small-Solar Powered Electronics | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Solar |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-photovoltaic-equipment | https://www.sgls.sec.org.sg/categoryinfo.php?cid=71
Singapore Green Labelling Scheme: Refrigerators and Freezers | This category establishes criteria for electric household refrigerators (with or without low-temperature compartment), refrigerator-freezer combinations and freezers (chest and upright freezers) used as free-standing, built-under or built-in appliances. | Singapore* | Refrigerators-Freezers | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-refrigerators-and-freezers | https://www.sgls.sec.org.sg/
Singapore Green Labelling Scheme: Solar-Powered Products | The scope of certification under this category includes solar powered products such as watches/clocks, caliper gauges, desktop and pocket calculators, scales for small utilisation, e.g. letter, parcel, bathroom and kitchen scales, titrating devices, toys, solar construction kits, solar training kits, and solar experimental kits. | Singapore* | Small-Solar Powered Electronics, Solar Energy Kits | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Solar |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/policies/singapore-green-labelling-scheme-solar-powered-products | https://www.sgls.sec.org.sg/categoryinfo.php?cid=62