## Policy Search
Policy | Description | Geography | Products Type | Policy Approach | Policy Instrument | Policy Status | Adopted | Revised | Updated by CLASP | Fuel Types | Test Method Applied | Responsible Agency | Related Topics | Permalink | Source
Energy Conservation (Regulated Goods and Registered Suppliers) Regulations 2017 | This regulation specifies the MEPS and labeling requirements for air‑conditioners; single-phase clothes dryers; single-phase lamps; ballasts for fluorescent lamps; single-phase refrigerators without freezers, refrigerators with freezers, and refrigerators with freezers and through-the-door ice dispensers; single‑phase televisions; and single speed three-phase 50 Hz induction motors. | Singapore* | Televisions, Clothes Dryers, Non-Directional lamps, Directional Lamps, Fluorescent and HID Lighting, 3-Phase Motors, Room ACs - Stationary ACs, Refrigerators-Freezers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised |  |  | October 2022 | Electricity | Single-phase non-ducted room air conditioners: ISO 5151:2017, ISO 15042:2017 , Refrigerators: ISO 15502:2005; IEC 62552:2007 , Clothes Dryers: IEC 61121:2005 , Televisions: IEC 62087:2008 , General Lighting: CIE 84:1989; IEC 60064 , Three-phase VRF air-conditioners: ISO 15042:2017 , Three-phase induction motors: IEC 60032:2014 | Minister for the Environment and Water Resources | Energy Efficiency | https://cprc-clasp.ngo/policies/energy-conservation-regulated-goods-and-registered-suppliers-regulations-2017 | https://sso.agc.gov.sg/Act/ECA2012/Uncommenced/20171227?ValidDt=20180101&ViewType=Sl
MELS for Casement and Window Air-Conditioners | This policy defines the minimum energy labeling scheme for casement and window air-conditioners up to 8.8kW. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | New | 2008 | 2014 | December 2023 | Electricity | ISO 5151:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Split Type Air-Conditioners | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | Revised | 2008 | 2014 | December 2023 | Electricity | ISO 15042:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-split-type-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MEPS for casement and window air-conditioners | This policy applies to casement and window (up to 8.8 kW). The Minimum Coefficient of Performance (COP) is set at COP100% > 3.78. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards: ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2022 | December 2023 | Electricity | ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners (2022) | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. The established MEPS are: Single/Multi Split (inverter) up to 17.6kW: COP100% ≥ 3.34 Single/Multi Split (inverter) up to 17.6kW: COPweighted ≥ 4.04 Single/Multi Split (non-inverter) up to 17.6kW: COP100% ≥ 4.04 COPweighted = 0.4 x COP100% + 0.6 x COP50% | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Revised, Superseded | 2011 | 2022 | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , ISO 5151:2017, Section 5.1: Cooling capacity test, Climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011, Climate class Nil | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-split-type-air-conditioners-2022 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners (2025) | This policy raises MEPS for single and multi split air conditioners. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2025 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-split-type-air-conditioners-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
SASO 2663:2018 MEPS and labeling schemes for small air conditioners | This standard applies to single-package window type, single split-system non-ducted air conditioners using air-cooled condensers, single split-system ducted airconditioners using air-cooled condensers, and heat pumps using aircooled condensers or using electric resistance for residential, commercial and industrial sector as applicable. | Kingdom of Saudi Arabia | Room ACs - Stationary ACs | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2013 | 2018 | November 2019 | Electricity | SASO 2681 / 2013 (based on ISO 5151) SASO 2682/2013 SASO 2763/2008 | Saudi Standard, Metrology and Quality Organization | Energy Efficiency | https://cprc-clasp.ngo/policies/saso-26632018-meps-and-labeling-schemes-small-air-conditioners | https://saso.gov.sa/ar/mediacenter/events/Pages/default.aspx
SASO 2874:2016 MEPS for large air conditioners | This standard specifies the MEPS and testing requirements for electrically operated air conditioners, condensing units, chillers, absorption chillers, electrically operated variable refrigerant flow (VRF) air conditioners, close control air conditioners and condensing units serving computer rooms. | Kingdom of Saudi Arabia | Room ACs - Stationary ACs, Chillers - Cooler Towers | Mandatory | Minimum Performance Standard | Entered into force, New | 2016 |  | November 2019 | Electricity |  | Saudi Standard, Metrology and Quality Organization | Energy Efficiency | https://cprc-clasp.ngo/policies/saso-28742016-meps-large-air-conditioners | https://www.intertek.com.cn/Uploadfile/File/SASO-2874_2016.pdf