## Policy Search
Policy | Description | Geography | Products Type | Policy Approach | Policy Instrument | Policy Status | Adopted | Revised | Updated by CLASP | Fuel Types | Test Method Applied | Responsible Agency | Related Topics | Permalink | Source
Energy Conservation (Regulated Goods and Registered Suppliers) Regulations 2017 | This regulation specifies the MEPS and labeling requirements for air‑conditioners; single-phase clothes dryers; single-phase lamps; ballasts for fluorescent lamps; single-phase refrigerators without freezers, refrigerators with freezers, and refrigerators with freezers and through-the-door ice dispensers; single‑phase televisions; and single speed three-phase 50 Hz induction motors. | Singapore* | Televisions, Clothes Dryers, Non-Directional lamps, Directional Lamps, Fluorescent and HID Lighting, 3-Phase Motors, Room ACs - Stationary ACs, Refrigerators-Freezers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised |  |  | October 2022 | Electricity | Single-phase non-ducted room air conditioners: ISO 5151:2017, ISO 15042:2017 , Refrigerators: ISO 15502:2005; IEC 62552:2007 , Clothes Dryers: IEC 61121:2005 , Televisions: IEC 62087:2008 , General Lighting: CIE 84:1989; IEC 60064 , Three-phase VRF air-conditioners: ISO 15042:2017 , Three-phase induction motors: IEC 60032:2014 | Minister for the Environment and Water Resources | Energy Efficiency | https://cprc-clasp.ngo/policies/energy-conservation-regulated-goods-and-registered-suppliers-regulations-2017 | https://sso.agc.gov.sg/Act/ECA2012/Uncommenced/20171227?ValidDt=20180101&ViewType=Sl
ISIRI 10634 Fans- Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Fans with capacity of 170-3500 m3 per h. Does not cover ceiling fans or portable fans. | Iran | Industrial Fans | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2008 | 2010 | January 2016 | Electricity | ANSI/ASHRAE 51-1999 (AMCA Standard 210-99 ANSI approved) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/policies/isiri-10634-fans-technical-specifications-and-test-methods-energy-consumption-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10636 Specification for Energy Consumption and Energy labeling of Fan coils and Ducted fan coils | Ducted and non-ducted fan coil room air conditioners | Iran | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2008 | 2006 | January 2016 | Electricity | ANSI/ASHRAE STANDARD 79-2002, ARI 440-1998 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-10636-specification-energy-consumption-and-energy-labeling-fan-coils-and-ducted-fan | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10638 -Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Single package non ducted single and multi split Product sub-type is yet to be determined. | Iran | Room ACs - Stationary ACs | Mandatory | Comparative Label | Entered into force, New | 2009 |  | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-10638-technical-specifications-and-test-methods-energy-consumption-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 11574 Central Station Air Handling Units-Specification and Test Methids for Energy Consumption | This policy covers air units with capacity of 3570m3/h to 34000m3/h. | Iran | Central ACs | Mandatory | Minimum Performance Standard | Entered into force, New | 2009 |  | January 2016 | Electricity | ARI 430-1999, ANSI/AMCA210/ASHRAE 51-2007, ARI 410-2001, ARI 410-2000 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/policies/isiri-11574-central-station-air-handling-units-specification-and-test-methids-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 1220-2- Test Methods for Energy Consumption and Energy Labelling Instructions | Gas fired space heaters with chimney with maximum consumption less than 150 MegaJolt per hr | Iran | Boilers and Furnaces | Mandatory | Comparative Label | Entered into force, Revised | 2002 | 2002 | January 2016 | Gas | AS 4553, | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-1220-2-test-methods-energy-consumption-and-energy-labelling-instructions | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 12885, 1st Edition- technical specification and test method for energy consumption and energy labeling instruction | Gas fired forced convection air heaters for space heating not exceeding a net heat input of 300 kW | Iran | Boilers and Furnaces | Mandatory | Minimum Performance Standard | Entered into force, Revised | 1998 | 2009 | January 2016 | Gas | BS EN 1020 1998, AS 4553& AG 103 2000: | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/policies/isiri-12885-1st-edition-technical-specification-and-test-method-energy-consumption-and | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 13782, Amendment No.1 , Boilers - Technical specifications and test method for energy consumption and energy labeling instruction | BoilersTechnical Specifications and Test Method for Energy Consumption and Energy Labeling Instruction | Iran | Boilers and Furnaces | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2011 | 2015 | January 2020 | Electricity | ISIRI 4231 ,ASME PTC4 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-13782-amendment-no1-boilers-technical-specifications-and-test-method-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 14629:2011-determination of critera for energy consumption and energy labeling instruction | centeral heating boilers of nominal heat input not exceeeding 70 kw -nominal heat input not exceeding 70kW | Iran | Boilers and Furnaces | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2013 | January 2016 | Gas |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-146292011-determination-critera-energy-consumption-and-energy-labeling-instruction | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 3678-2: 2002, 1st Edition- Method for measuring of energy consumption and energy labeling instructions | This policy applies to liquid chilling packages with water-cooled condenser and evaporator. | Iran | Chillers - Cooler Towers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2002 | 2002 | January 2016 | Electricity | NS 3678: 1995 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-3678-2-2002-1st-edition-method-measuring-energy-consumption-and-energy-labeling | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 4910-2, 1st Revision- Method for measuring of energy consumption and energy labeling instructions | Evaporative air coolers -Direct and indirect types | Iran | Evaporative Coolers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 1999 | 2009 | January 2016 | Electricity | AS 2913-1987 ,IS3315-1974 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-4910-2-1st-revision-method-measuring-energy-consumption-and-energy-labeling | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 6016-2 | Split-system non-ducted air conditioners and heat pumps - method for measuring of energy consumption and energy labeling instruction | Iran | Room ACs - Stationary ACs | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2002 |  | January 2016 | Electricity | ISIRI 6016, ISIRI 6016-2 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-6016-2 | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7268-2,Flueless gas room heaters - Technical specification and test method for energy consumption and energy labeling instruction | Gas fired space heaters without chimney with maximum consumption 30MegaJolt/Hr. | Iran | Boilers and Furnaces | Mandatory | Comparative Label | Entered into force, Revised | 2002 | 2010 | January 2016 | Gas | AS 4553, ISIRI 7268-1 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-7268-2flueless-gas-room-heaters-technical-specification-and-test-method-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7342-2, Specification for energy consumption and energy labeling of electric houshold room heaters | Residential electric space heater | Iran | Boilers and Furnaces | Mandatory | Comparative Label | Entered into force, Revised | 2002 | 2012 | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/policies/isiri-7342-2-specification-energy-consumption-and-energy-labeling-electric-houshold-room | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
MELS for Casement and Window Air-Conditioners | This policy defines the minimum energy labeling scheme for casement and window air-conditioners up to 8.8kW. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | New | 2008 | 2014 | December 2023 | Electricity | ISO 5151:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Portable Air-Conditioners (2024) | This policy defines the minimum energy labeling scheme for single-phase portable air-conditioners: | Singapore* | Portable ACs | Mandatory | Comparative Label | Entered into force, New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-portable-air-conditioners-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Split Type Air-Conditioners | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | Revised | 2008 | 2014 | December 2023 | Electricity | ISO 15042:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-split-type-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Three-Phase VRF Air-Conditioners | This policy defines the minimum energy labeling scheme requirements for base module/units of a three-phase VRF air-conditioners (unit efficiency) of all cooling capacities. | Singapore* | Central ACs | Mandatory | Comparative Label | New | 2021 |  | December 2023 | Electricity | ISO 15042:2017 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/mels-three-phase-vrf-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MEPS for casement and window air-conditioners | This policy applies to casement and window (up to 8.8 kW). The Minimum Coefficient of Performance (COP) is set at COP100% > 3.78. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards: ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2022 | December 2023 | Electricity | ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Portable Air-Conditioners (2024) | This policy regulates minimum energy performance standard for portable air conditioners. Single-phase portable air-conditioners having a single exhaust duct (up to 12 kW) should have Coefficient of Performance (COP) 100% equal or greater than 3.0. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards. 1 Weighted COP = 0.4 x COP100% + 0.6 x COP50% N is the number of indoor and outdoor units Standby power is expressed in Watts | Singapore* | Portable ACs | Mandatory | Minimum Performance Standard | New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-portable-air-conditioners-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. The established MEPS are: Single/Multi Split (inverter) up to 17.6kW: COP100% ≥ 3.34 Single/Multi Split (inverter) up to 17.6kW: COPweighted ≥ 4.04 Single/Multi Split (non-inverter) up to 17.6kW: COP100% ≥ 4.04 COPweighted = 0.4 x COP100% + 0.6 x COP50% | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Revised | 2011 | 2022 | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , ISO 5151:2017, Section 5.1: Cooling capacity test, Climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011, Climate class Nil | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-split-type-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners (2025) | This policy raises MEPS for single and multi split air conditioners. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2025 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-split-type-air-conditioners-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Three-Phase VRF Air-Conditioners | A base module/unit of a three-phase VRF air-conditioner (unit efficiency) of all cooling capacities must meet the following Minimum Integrated Energy Efficiency Ratio (IEER): ≥ 4.35. Integrated Energy Efficiency Ratio (IEER) = (0.020 x A) + (0.617 x B) + (0.238 x C) + (0.125 x D) where A = COP at full load cooling capacity tested under ISO 15042 T1 condition, B = COP at 75% part load cooling capacity tested under ISO 15042 T1 condition, C = COP at 50% part load cooling capacity tested under ISO 15042 T1 condition, D = COP at 25% part load cooling capacity tested under ISO 15042 T1 condition. | Singapore* | Central ACs | Mandatory | Minimum Performance Standard | New | 2021 |  | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/policies/meps-three-phase-vrf-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards