## Policy Search
Policy | Description | Geography | Products Type | Policy Approach | Policy Instrument | Policy Status | Adopted | Revised | Updated by CLASP | Fuel Types | Test Method Applied | Responsible Agency | Related Topics | Permalink | Source
Energy Conservation (Regulated Goods and Registered Suppliers) Regulations 2017 | This regulation specifies the MEPS and labeling requirements for air‑conditioners; single-phase clothes dryers; single-phase lamps; ballasts for fluorescent lamps; single-phase refrigerators without freezers, refrigerators with freezers, and refrigerators with freezers and through-the-door ice dispensers; single‑phase televisions; and single speed three-phase 50 Hz induction motors. | Singapore* | Televisions, Clothes Dryers, Non-Directional lamps, Directional Lamps, Fluorescent and HID Lighting, 3-Phase Motors, Room ACs - Stationary ACs, Refrigerators-Freezers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised |  |  | October 2022 | Electricity | Single-phase non-ducted room air conditioners: ISO 5151:2017, ISO 15042:2017 , Refrigerators: ISO 15502:2005; IEC 62552:2007 , Clothes Dryers: IEC 61121:2005 , Televisions: IEC 62087:2008 , General Lighting: CIE 84:1989; IEC 60064 , Three-phase VRF air-conditioners: ISO 15042:2017 , Three-phase induction motors: IEC 60032:2014 | Minister for the Environment and Water Resources | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/energy-conservation-regulated-goods-and-registered-suppliers-regulations-2017 | https://sso.agc.gov.sg/Act/ECA2012/Uncommenced/20171227?ValidDt=20180101&ViewType=Sl
ISIR 14577, 1st Edition, Household refrigerating appliances - Determination of Criteria for energy consumption and energy labeling instructions | Domestic refrigerator, freezer, refrigerator-freezer | Iran | Refrigerators-Freezers, Freezers-only | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 1998 | 2012 | January 2016 | Electricity | ISO-8187 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isir-14577-1st-edition-household-refrigerating-appliances-determination-criteria-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10634 Fans- Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Fans with capacity of 170-3500 m3 per h. Does not cover ceiling fans or portable fans. | Iran | Industrial Fans | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2008 | 2010 | January 2016 | Electricity | ANSI/ASHRAE 51-1999 (AMCA Standard 210-99 ANSI approved) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/isiri-10634-fans-technical-specifications-and-test-methods-energy-consumption-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10635: 2008, Wet Cooling Towers, Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Applicable to wet cooling towers with capacity of 800 tons. Does not include cooling towers with natural flow | Iran | Water Coolers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2002 | 2008 | January 2016 | Electricity | ISIRI 4514 (1998), BS EN 13741 (2003), BS 4485-part2 (1988), CTI ATC 105 (2000) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/isiri-10635-2008-wet-cooling-towers-technical-specifications-and-test-methods-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10636 Specification for Energy Consumption and Energy labeling of Fan coils and Ducted fan coils | Ducted and non-ducted fan coil room air conditioners | Iran | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2008 | 2006 | January 2016 | Electricity | ANSI/ASHRAE STANDARD 79-2002, ARI 440-1998 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-10636-specification-energy-consumption-and-energy-labeling-fan-coils-and-ducted-fan | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10637:2007,Refrigerated Display Cabinet-Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Refrigerated Display Cabinet. Does not include vending machines | Iran | Refrigerated Cabinets | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2007 | 2012 | January 2016 | Electricity | ISIRI 9187-2:2007 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-106372007refrigerated-display-cabinet-technical-specifications-and-test-methods | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10638 -Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Single package non ducted single and multi split Product sub-type is yet to be determined. | Iran | Room ACs - Stationary ACs | Mandatory | Comparative Label | Entered into force, New | 2009 |  | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-10638-technical-specifications-and-test-methods-energy-consumption-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10639: 2007,1st edition -Technical specifications and test method for energy consumption and energy labeling instruction | Residential hermetic compressor -one level, positive displacement compressor. Does not include high pressure hermetic compressor | Iran | Refrigerant Compressors | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2013 |  | January 2016 | Electricity | ISIRI NS 4335 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-10639-20071st-edition-technical-specifications-and-test-method-energy-consumption | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10641 Office Equipment-Technical Specifications for Energy Consumption and Energy Labeling Instructions | Includes desktop and personal computers, monitors, copy machines, multi devise machines, fax-printer-scanner; Fax, scanner, printer. Does not include server computers. | Iran | Imaging Equipment | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2012 | 2010 | January 2016 | Electricity | IEC 311 (1988) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-10641-office-equipment-technical-specifications-energy-consumption-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10672, Amendment No.1-Technical Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Electric Household Vaccum cleaner | Iran | Vacuum Cleaners | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2012 | 2014 | January 2016 | Electricity | NS 5635 (2001) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-10672-amendment-no1-technical-specifications-and-test-methods-energy-consumption-and | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 10759:2005, 1st Edition- technical specifications and test method for energy consumption and energy labeling instruction | Covers electric fluorescent ballast and tube fluorescent lamps 20-40 W, frequency 50hz, and 220-240 volts | Iran | Fluorescent and HID Lighting | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2009 |  | January 2016 | Electricity | 34C/682/INF: 2005, 34C/693/NP: 2005 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-107592005-1st-edition-technical-specifications-and-test-method-energy-consumption | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 11574 Central Station Air Handling Units-Specification and Test Methids for Energy Consumption | This policy covers air units with capacity of 3570m3/h to 34000m3/h. | Iran | Central ACs | Mandatory | Minimum Performance Standard | Entered into force, New | 2009 |  | January 2016 | Electricity | ARI 430-1999, ANSI/AMCA210/ASHRAE 51-2007, ARI 410-2001, ARI 410-2000 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/isiri-11574-central-station-air-handling-units-specification-and-test-methids-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 1219-2:2002- Test Method for Energy Consumption and Energy Labeling Instruction | Storage water heater | Iran | Storage Water Heaters | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2013 |  | January 2016 | Gas |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-1219-22002-test-method-energy-consumption-and-energy-labeling-instruction | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 1220-2- Test Methods for Energy Consumption and Energy Labelling Instructions | Gas fired space heaters with chimney with maximum consumption less than 150 MegaJolt per hr | Iran | Boilers and Furnaces | Mandatory | Comparative Label | Entered into force, Revised | 2002 | 2002 | January 2016 | Gas | AS 4553, | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-1220-2-test-methods-energy-consumption-and-energy-labelling-instructions | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 12885, 1st Edition- technical specification and test method for energy consumption and energy labeling instruction | Gas fired forced convection air heaters for space heating not exceeding a net heat input of 300 kW | Iran | Boilers and Furnaces | Mandatory | Minimum Performance Standard | Entered into force, Revised | 1998 | 2009 | January 2016 | Gas | BS EN 1020 1998, AS 4553& AG 103 2000: | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/isiri-12885-1st-edition-technical-specification-and-test-method-energy-consumption-and | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 13368 Energy Consumption Criteria for Oil Distribution Transformers | Three Phases oil transformers, less than 36kVA and 25kVA up to 2500kVA ,50Hz | Iran | Power Transformers | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity | IEC 60071-1, 2011, IEC 60071-2, 2011 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/isiri-13368-energy-consumption-criteria-oil-distribution-transformers | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 13782, Amendment No.1 , Boilers - Technical specifications and test method for energy consumption and energy labeling instruction | BoilersTechnical Specifications and Test Method for Energy Consumption and Energy Labeling Instruction | Iran | Boilers and Furnaces | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2011 | 2015 | January 2020 | Electricity | ISIRI 4231 ,ASME PTC4 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-13782-amendment-no1-boilers-technical-specifications-and-test-method-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 14628-Determination of Criteria for energy consumption and energy labeling instruction | Covers air units with capacity of 3570m3 per h to 34000m3 per h | Iran | Cooktops or Hobs | Mandatory | Minimum Performance Standard | Entered into force, New | 2013 |  | January 2016 | Gas | ISIRI 10335 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-14628-determination-criteria-energy-consumption-and-energy-labeling-instruction | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 14629:2011-determination of critera for energy consumption and energy labeling instruction | centeral heating boilers of nominal heat input not exceeeding 70 kw -nominal heat input not exceeding 70kW | Iran | Boilers and Furnaces | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2013 | January 2016 | Gas |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-146292011-determination-critera-energy-consumption-and-energy-labeling-instruction | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 1563-2:2009, 1st Revision, Specification for energy consumption and energy labeling of electrical household water heaters | Standard includes electrical household water heaters. Does not include solar or coal water heaters. Does not include residential electric water heaters with capacity less than 50L and more than 120L. | Iran | Storage Water Heaters | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2009 |  | January 2016 | Electricity | IEC 379: 1987 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-1563-22009-1st-revision-specification-energy-consumption-and-energy-labeling | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 16163:2013-determination of criteria for energy consumption and labeling instruction | Residential electric dishwasher | Iran | Dishwashers | Mandatory | Minimum Performance Standard | Entered into force, New | 2013 |  | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-161632013-determination-criteria-energy-consumption-and-labeling-instruction | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 1828-2-Test Methods for Energy Consumption and Energy Labelling Instructions | Instantaneous gas water heaters with maximum consumtion less than 250MegaJolt per Hr | Iran | Instantaneous Water Heaters | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2003 | 2010 | January 2016 | Gas | AG 102: 2000, EN 26: 2000, ISIRI 1828-1 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-1828-2-test-methods-energy-consumption-and-energy-labelling-instructions | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 3477-2, 1st Edition, Specification for energy consumption and energy labeling of electrical household washing machines | Fully automatic residential clothes washer | Iran | Washing Machines | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2002 |  | January 2016 | Electricity | 95/12/EC | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-3477-2-1st-edition-specification-energy-consumption-and-energy-labeling-electrical | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 3678-2: 2002, 1st Edition- Method for measuring of energy consumption and energy labeling instructions | This policy applies to liquid chilling packages with water-cooled condenser and evaporator. | Iran | Chillers - Cooler Towers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2002 | 2002 | January 2016 | Electricity | NS 3678: 1995 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-3678-2-2002-1st-edition-method-measuring-energy-consumption-and-energy-labeling | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 4910-2, 1st Revision- Method for measuring of energy consumption and energy labeling instructions | Evaporative air coolers -Direct and indirect types | Iran | Evaporative Coolers | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 1999 | 2009 | January 2016 | Electricity | AS 2913-1987 ,IS3315-1974 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-4910-2-1st-revision-method-measuring-energy-consumption-and-energy-labeling | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 5916 Self Ballasted Lamps for General Lighting Services-performance requirements | Covers multi sector self ballasted lamps (60W and 100-250V) | Iran | Non-Directional lamps | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2004 |  | January 2016 | Electricity | IEC 60968 and IEC 60969 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-5916-self-ballasted-lamps-general-lighting-services-performance-requirements | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 6016-2 | Split-system non-ducted air conditioners and heat pumps - method for measuring of energy consumption and energy labeling instruction | Iran | Room ACs - Stationary ACs | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2002 |  | January 2016 | Electricity | ISIRI 6016, ISIRI 6016-2 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-6016-2 | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7268-2,Flueless gas room heaters - Technical specification and test method for energy consumption and energy labeling instruction | Gas fired space heaters without chimney with maximum consumption 30MegaJolt/Hr. | Iran | Boilers and Furnaces | Mandatory | Comparative Label | Entered into force, Revised | 2002 | 2010 | January 2016 | Gas | AS 4553, ISIRI 7268-1 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-7268-2flueless-gas-room-heaters-technical-specification-and-test-method-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7342-2, Specification for energy consumption and energy labeling of electric houshold room heaters | Residential electric space heater | Iran | Boilers and Furnaces | Mandatory | Comparative Label | Entered into force, Revised | 2002 | 2012 | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-7342-2-specification-energy-consumption-and-energy-labeling-electric-houshold-room | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7817-2, 1st Edition, Centrifugal, mixed flow and axial pumps - Method for measuring of energy consumption and energy labeling instructions | Centrifugal, mixed flow and axial pumps | Iran | Pumps Other | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2002 | 2002 | January 2016 | Electricity | ISO-2548 (Class C) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/isiri-7817-2-1st-edition-centrifugal-mixed-flow-and-axial-pumps-method-measuring-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7872:2009, 1st Rev, Household electric iron energy consumption requirements and energy labeling guideline | Covers residential steam and non-steam irons. Does not include residential press irons | Iran | Irons | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2009 |  | January 2016 | Electricity | IEC 311 (1988) | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-78722009-1st-rev-household-electric-iron-energy-consumption-requirements-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7874, 1st Edition, Specification for energy consumption and energy labeling of single phase electrical motors | Small 1-phase General Purpose | Iran | 1-Phase Motors | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity | ISIRI 3772-1 | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-7874-1st-edition-specification-energy-consumption-and-energy-labeling-single-phase | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7875-1st edition- Specifications and Test Methods for Energy Consumption and Energy Labeling Instructions | Includes electric kettles with capacity of minimum 4L and maximum 30L with 250 Va.c. | Iran | Electric Kettles | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-7875-1st-edition-specifications-and-test-methods-energy-consumption-and-energy | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI 7966, 1st Edition, Specification for energy consumption and energy labeling of three phase electrical motors | This policy covers all motors with 3 phase general purpose | Iran | 3-Phase Motors | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-7966-1st-edition-specification-energy-consumption-and-energy-labeling-three-phase | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
ISIRI NS 7341, 1st edition- Technical specifications and test method for energy consumption and energy labeling instruction | Electric lamps - Tubular, double capped | Iran | Tubular Lamps | Mandatory | Comparative Label, Minimum Performance Standard | Entered into force, New | 2004 |  | January 2016 | Electricity | NS687 (Double Capped), NS 2702 (High Pressure Mercury Vapor), NS 5191 (HPSI), NS 5211 (Single Capped), 98/11/EC | Institute of Standards and Industrial Research of Iran (ISIRI) | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/isiri-ns-7341-1st-edition-technical-specifications-and-test-method-energy-consumption-and | http://isiri.gov.ir/portal/home/?135546/%D8%A7%D8%B7%D9%84%D8%A7%D8%B9%D8%A7%D8%AA-%D9%85%D8%B1%D8%A8%D9%88%D8%B7-%D8%A8%D9%87-%D8%A7%D8%B3%D8%AA%D8%A7%D9%86%D8%AF%D8%A7%D8%B1%D8%AF%D9%87%D8%A7%DB%8C-%D8%A8%D8%B1%DA%86%D8%B3%D8%A8-%D8%A7%D9%86%D8%B1%DA%98%
MELS for Casement and Window Air-Conditioners | This policy defines the minimum energy labeling scheme for casement and window air-conditioners up to 8.8kW. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | New | 2008 | 2014 | December 2023 | Electricity | ISO 5151:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Clothes Dryers | This policy defines minimum energy labeling scheme (MELS) requirements for clothes dryers with a rated capacity of up to 10kg. Energy Consumption (EC) per wash in kWh (all clothes dryers) - 1 tick: NA - 2 tick: Rated capacity x 0.55 ≥ EC > Rated capacity x 0.45 - 3 tick: Rated capacity x 0.45 ≥ EC > Rated capacity x 0.37 - 4 tick: Rated capacity x 0.37 ≥ EC > Rated capacity x 0.30 - 5 tick: Rated capacity x 0.30 ≥ EC Rated Capacity means the mass in kilograms of a particular type of dry textiles which, according to the instructions of the manufacturer of the clothes dryer, can be treated in a particular drying program suitable for drying the particular type of dry textile. | Singapore* | Clothes Dryers | Mandatory | Comparative Label | Revised | 2009 | 2014 | December 2023 | Electricity | IEC 61121:2005 with amendment 1 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-clothes-dryers | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Commercial Storage Refrigerators | This policy defines minimum energy labeling scheme requirements for chiller, freezers, and combinations type of all capacities. | Singapore* | Refrigerated Cabinets, Wine Chillers, Walk-In Coolers and Freezers, Refrigerated Vending Machines, Freezers-only | Mandatory | Comparative Label | Entered into force, New | 2025 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-commercial-storage-refrigerators | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for General Lighting | This policy defines minimum energy labeling scheme requirements for incandescent lamps, CFLi lamps, and LEDs with an Edison screw or a bayonet lamp cap. | Singapore* | Tubular Lamps, Non-Directional lamps | Mandatory | Comparative Label | Revised | 2015 | 2019 | December 2023 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-general-lighting | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for General Lighting (2024) | This policy set energy label scheme for all regulated lamps: | Singapore* | Tubular Lamps, Non-Directional lamps | Mandatory | Comparative Label | Entered into force, Revised | 2015 | 2024 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-general-lighting-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Portable Air-Conditioners (2024) | This policy defines the minimum energy labeling scheme for single-phase portable air-conditioners: | Singapore* | Portable ACs | Mandatory | Comparative Label | Entered into force, New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-portable-air-conditioners-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Refrigerators | This policy defines minimum energy labeling scheme requirements for the following products: - Refrigerators without a freezer up to 900L - Refrigerators with a freezer up to 300L - Refrigerators with a freezer > 300L to 900L - Refrigerators with freezer and through-the-door ice dispenser | Singapore* | Refrigerators-Freezers | Mandatory | Comparative Label | New | 2008 | 2014 | December 2023 | Electricity | IEC 62552:2007 , ISO 15502:2005 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-refrigerators | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Split Type Air-Conditioners | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. | Singapore* | Room ACs - Stationary ACs | Mandatory | Comparative Label | Revised | 2008 | 2014 | December 2023 | Electricity | ISO 15042:2017 , IEC 62301:2005 , IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-split-type-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Televisions | This policy contains minimum energy labeling scheme (MELS) requirements for televisions. | Singapore* | Televisions | Mandatory | Comparative Label | New | 2014 |  | December 2023 | Electricity | IEC 62087:2008 , IEC 62087:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-televisions | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Three-Phase VRF Air-Conditioners | This policy defines the minimum energy labeling scheme requirements for base module/units of a three-phase VRF air-conditioners (unit efficiency) of all cooling capacities. | Singapore* | Central ACs | Mandatory | Comparative Label | New | 2021 |  | December 2023 | Electricity | ISO 15042:2017 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-three-phase-vrf-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MELS for Water Heater | This policy defines minimum energy labeling scheme requirements for all regulated water heaters: | Singapore* | Instantaneous Water Heaters, Storage Water Heaters | Mandatory | Comparative Label | Entered into force, New | 2025 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/mels-water-heater | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/tick-rating
MEPS and labeling schemes for air conditioners | Information not available | Guyana | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard, Comparative Label | Under development |  |  | October 2019 | Electricity |  | Energy Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-and-labeling-schemes-air-conditioners-3 | https://caricom.org/media-center/communications/news-from-the-community/guyana-standards-bureau-working-with-crosq-on-energy-efficiency-standard
MEPS and labeling schemes for lighting products | Information not available | Guyana | Directional Lamps | Mandatory | Minimum Performance Standard, Comparative Label | Under development |  |  | October 2019 | Electricity |  | Energy Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-and-labeling-schemes-lighting-products-1 | https://caricom.org/media-center/communications/news-from-the-community/guyana-standards-bureau-working-with-crosq-on-energy-efficiency-standard
MEPS and labeling schemes for refrigerators | Information not available | Guyana | Refrigerators-Freezers | Mandatory | Comparative Label, Minimum Performance Standard | Under development |  |  | October 2019 | Electricity |  | Guyana Energy Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-and-labeling-schemes-refrigerators | https://caricom.org/media-center/communications/news-from-the-community/guyana-standards-bureau-working-with-crosq-on-energy-efficiency-standard
MEPS for casement and window air-conditioners | This policy applies to casement and window (up to 8.8 kW). The Minimum Coefficient of Performance (COP) is set at COP100% > 3.78. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards: ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2022 | December 2023 | Electricity | ISO 5151:2017, Section 5.1: Cooling capacity test, Climate Class T1 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-casement-and-window-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Clothes Dryers | This policy defines minimum energy performance requirements for clothes dryers with a rated capacity of https://www.nea.gov.sg/up to 10kg. The revised 2022 MEPS are: EC ≤ [Rated Capacity x 0.55], where “Rated Capacity” means the mass in kilograms of a particular type of dry textiles which, according to the instructions of the manufacturer of the clothes dryer, can be treated in a particular drying program suitable for drying the particular type of dry textile and “EC” means Energy Consumption in kWh per wash. | Singapore* | Clothes Dryers | Mandatory | Minimum Performance Standard | Revised | 2014 | 2022 | December 2023 | Electricity | IEC1 61121:2005 with amendment 1, Section 9.2.1: Drying tests general | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-clothes-dryers | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Commercial Storage Refrigerators (2025) | This policy sets minimum energy performance standards for commercial storage refrigerators as shown below | Singapore* | Refrigerated Cabinets, Wine Chillers, Walk-In Coolers and Freezers, Refrigerated Vending Machines, Freezers-only | Mandatory | Minimum Performance Standard | Entered into force, New | 2025 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-commercial-storage-refrigerators-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for General Lighting | This policy sets minimum energy performance requirements for the following products: incandescent lamps (25-200W), Compact fluorescent lamps with integrated ballast (CFLi) (up to 60W), LED lamps with an Edison screw or a bayonet lamp cap (up to 60W), Compact fluorescent lamps without integrated ballast (CFLni), T8 Linear, double-capped, fluorescent lamps (LFL)[0.5 - 1.5]m, and LED lamps designed as a direct replacement for CFLni and T8 LFL without requiring any internal modification of the luminaires. | Singapore* | Lighting, Lamps, Tubular Lamps, Non-Directional lamps, HD lamps and retrofits | Mandatory | Minimum Performance Standard | Revised | 2015 | 2019 | December 2023 | Electricity | CIE3 84:1989 and IEC 60064, Measurement of luminous flux , CIE 84:1989 and IEC 60064 or IEC 60357, Measurement of luminous flux , IEC 60969:2001, Performance tests , IEC 60901:2001, Performance tests , IEC 60081:2002, Performance tests , IEC 62612:2013, Performance tests , IEC 62612:2013, Performance tests | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-general-lighting | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for General Lighting (2024) | This policy sets minimum energy performance standards for lamps as shown below | Singapore* | Tubular Lamps, Non-Directional lamps | Mandatory | Minimum Performance Standard | Revised | 2015 | 2024 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-general-lighting-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Portable Air-Conditioners (2024) | This policy regulates minimum energy performance standard for portable air conditioners. Single-phase portable air-conditioners having a single exhaust duct (up to 12 kW) should have Coefficient of Performance (COP) 100% equal or greater than 3.0. Cooling capacity refers to the measured total cooling capacity in accordance with the applicable test standards. 1 Weighted COP = 0.4 x COP100% + 0.6 x COP50% N is the number of indoor and outdoor units Standby power is expressed in Watts | Singapore* | Portable ACs | Mandatory | Minimum Performance Standard | New | 2024 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-portable-air-conditioners-2024 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Refrigerators | This policy defines minimum energy performance requirements for the following refrigerators: - Refrigerators without a freezer up to 900L: - Refrigerators with a freezer up to 300L: AEC ≤ [(465 + 1.378 xVadj tot) x 0.427] - Refrigerators with a freezer > 300L to 900L: AEC ≤ [(465 + 1.378 xVadj tot) x 0.427] - Refrigerators with freezer and through-the-door ice dispenser: AEC ≤ [(585 + 1.378 x Vadj tot) x 0.409] - Vadj tot is defined as the sum of the adjusted volumes of the refrigerator compartments. - “Through-the-door ice dispenser” means an automatic ice maker coupled with a device that delivers ice on demand externally through a door. - “AEC” means Annual Energy Consumption. | Singapore* | Refrigerators-Freezers | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2022 | December 2023 | Electricity | IEC 62552:2007 or ISO2 15502:2005, Section 15: Energy consumption test, climate class T | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-refrigerators-0 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Refrigerators (2025) | This policy raises minimum energy performance standards for refrigerators with adjusted volumes no greater than 900 litres. | Singapore* | Refrigerators-Freezers | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2025 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-refrigerators-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners | This policy applies to any single-phase non-ducted room air-conditioner (split type (inverter)) with a cooling capacity of 17.6 kW or lower and any single-phase non-ducted room air-conditioner (split type (non-inverter)) with a cooling capacity of 17.6 kW or lower. The established MEPS are: Single/Multi Split (inverter) up to 17.6kW: COP100% ≥ 3.34 Single/Multi Split (inverter) up to 17.6kW: COPweighted ≥ 4.04 Single/Multi Split (non-inverter) up to 17.6kW: COP100% ≥ 4.04 COPweighted = 0.4 x COP100% + 0.6 x COP50% | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Revised | 2011 | 2022 | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , ISO 5151:2017, Section 5.1: Cooling capacity test, Climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011, Climate class Nil | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-split-type-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Split Type Air-Conditioners (2025) | This policy raises MEPS for single and multi split air conditioners. | Singapore* | Room ACs - Stationary ACs | Mandatory | Minimum Performance Standard | Entered into force, Revised | 2011 | 2025 | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-split-type-air-conditioners-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Televisions (2024/2025) | This policy sets minimum energy performance standards for non-8K TV at 4-tick and 8K TV at 3-tick, effective in April 2024, and April 2025 respectively, as shown below | Singapore* | Televisions | Mandatory | Minimum Performance Standard | Entered into force, New |  |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-televisions-20242025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Three-Phase Induction Motors | This policy applies to three-phase induction motors with a rated output from 0.75kW to 200kW and three-phase induction motors with a rated output >200kW to ≤ 375kW. | Singapore* | 3-Phase Motors | Mandatory | Minimum Performance Standard | New | 2018 |  | December 2023 | Electricity | IEC 60034-2-1 (2014), Method 2-1-1B , IEEE 112 (2004), Method B | National Environment Agency | Energy Efficiency, Industrial Sector | https://cprc-clasp.ngo/index.php/policies/meps-three-phase-induction-motors | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
MEPS for Three-Phase VRF Air-Conditioners | A base module/unit of a three-phase VRF air-conditioner (unit efficiency) of all cooling capacities must meet the following Minimum Integrated Energy Efficiency Ratio (IEER): ≥ 4.35. Integrated Energy Efficiency Ratio (IEER) = (0.020 x A) + (0.617 x B) + (0.238 x C) + (0.125 x D) where A = COP at full load cooling capacity tested under ISO 15042 T1 condition, B = COP at 75% part load cooling capacity tested under ISO 15042 T1 condition, C = COP at 50% part load cooling capacity tested under ISO 15042 T1 condition, D = COP at 25% part load cooling capacity tested under ISO 15042 T1 condition. | Singapore* | Central ACs | Mandatory | Minimum Performance Standard | New | 2021 |  | December 2023 | Electricity | ISO 15042:2017, Section 6.1: Cooling capacity test, climate class T1 , IEC 62301:2005 or IEC 62301:2011, Section 5.3.1 or 5.3.2 of IEC 62301:2005 or Section 5.3.2, 5.3.3 or 5.3.4 of IEC 62301:2011 | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-three-phase-vrf-air-conditioners | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/about-mandatory-energy-labelling-and-minimum-energy-performance-standards
MEPS for Water Heater (2025) | This policy sets minimum energy performance standards for water heaters as shown below | Singapore* | Instantaneous Water Heaters, Storage Water Heaters | Mandatory | Minimum Performance Standard | Entered into force, New | 2025 |  | September 2025 | Electricity |  | National Environment Agency | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/meps-water-heater-2025 | https://www.nea.gov.sg/our-services/climate-change-energy-efficiency/energy-efficiency/household-sector/minimum-energy-performance-standards
Singapore Green Labeling Scheme: CFLs | This standard establishes requirements for integral compact fluorescent lamps (CFL) where the tube and ballast are combined into a single unit. These lamps allow consumers to replace incandescent lamps easily with CFL. The product group that is within the scope of certification would include screw-based lamps with ballast and adaptor in a single assembly. | Singapore* | Non-Directional lamps, Directional Lamps | Voluntary | Endorsement Label | Entered into force, New | 2012 |  | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labeling-scheme-cfls | https://www.sgls.sec.org.sg/categoryinfo.php?cid=7
Singapore Green Labeling Scheme: Hand Dryers | This policy establishes criteria for electric hot air hand driers that are equipped with non-contact on-off switches based on environmental, performance, and health parameters. | Singapore* | Other | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labeling-scheme-hand-dryers | https://www.sgls.sec.org.sg/categoryinfo.php?cid=49
Singapore Green Labeling Scheme: Microwave Ovens | This policy establishes criteria for microwave ovens for household use. A microwave oven is an electrical appliance intended for household use that uses high-frequency electromagnetic waves for heating food or beverages, with a rated voltage of not more than 250 V and a frequency ranging from 890 MHz to 6 GHz. | Singapore* | Microwaves | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labeling-scheme-microwave-ovens | https://www.sgls.sec.org.sg/categoryinfo.php?cid=81
Singapore Green Labeling Scheme: Personal Computers | This policy establishes criteria to label Personal Computers (PCs). These criteria include requirements for the following with a rated voltage of not more than 250 VAC: computer system unit; display (monitor); personal computer set combination system including units Computer System Unit, display (monitor), keyboard, and mouse; and portable computer such as notebook (notebook or laptop), tablet (tablet or slate). | Singapore* | Information Technology | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labeling-scheme-personal-computers | https://www.sgls.sec.org.sg/categoryinfo.php?cid=82
Singapore Green Labeling Scheme: Photocopiers, Printers, Fax Machines & Multifunctional Devices | This policy establishes grading criteria for Copying Machines, Printers, Fax Machines, and Multifunctional Devices (MFDs) based on environmental, performance, and health parameters. These criteria include requirements for standard-sized monochromatic and color office machines based on electrophotography (including laser and LED) and inkjet marking technologies. Standard-sized machines are those that primarily print or copy on regular-sized (e.g., A4 / 8.5 x 11) paper and envelopes. Large-format office machines are also included in this category. | Singapore* | Other-Electronics | Voluntary | Endorsement Label | Entered into force |  |  | October 2022 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labeling-scheme-photocopiers-printers-fax-machines-multifunctional-devices | https://www.sgls.sec.org.sg/categoryinfo.php?cid=38
Singapore Green Labeling Scheme: Televisions Sets | This category establishes criteria for mains-powered television sets consisting of a unit whose main purpose is to receive, reproduce and, if applicable, decode television signals. | Singapore* | Televisions | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labeling-scheme-televisions-sets | https://www.sgls.sec.org.sg/
Singapore Green Labelling Scheme: Coffee Machine | This category establishes criteria for espresso and coffee machines, which include fully-automatic espresso/coffee machines, hand-operated piston espresso/coffee machines and capsule espresso/coffee machines. The category does not cover espresso/coffee machines with a system to warm cups, or capsule espresso/coffee machines which require capsules made by a certain manufacturer. | Singapore* | Coffee Machines | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-coffee-machine | https://www.sgls.sec.org.sg/categoryinfo.php?cid=56
Singapore Green Labelling Scheme: Dishwashers | This category establishes criteria for dishwashers designed to be stand-alone on floors or counter surfaces meant for household use. They apply to devices which serve the function of dishwashing alone or in combination with other functions. | Singapore* | Dishwashers | Voluntary | Endorsement Label | Entered into force, New | 2013 |  | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-dishwashers | https://www.sgls.sec.org.sg/categoryinfo.php?cid=76
Singapore Green Labelling Scheme: Electric Kettles | This category establishes criteria for electric kettles for household use based on environmental, performance and health parameters. | Singapore* | Electric Kettles | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-electric-kettles | https://www.sgls.sec.org.sg/categoryinfo.php?cid=55
Singapore Green Labelling Scheme: Gas Cookers and Gas-fired Appliances | This category establishes criteria for household gas-powered cooking devices that are isolated in design i.e. individual machines (which operate with gas burners located on steel originated or glass and ceramic layered cooker top) and gas-powered cooking devices with built-in ovens (the latter may be either natural gas or electricity powered). This category does not include gas powered cooking devices which operate with gas burners located below a glass and ceramic layered cooker top. | Singapore* | Cooktops or Hobs | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Gas |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-gas-cookers-and-gas-fired-appliances | https://www.sgls.sec.org.sg/categoryinfo.php?cid=57
Singapore Green Labelling Scheme: Hot Water Storage Tanks | This scope for certification under this category includes hot-water storage tanks such as thermal solar systems and components, including water heaters, water heating installations, and storage water heaters for drinking water. | Singapore* | Storage Water Heaters | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Electricity, Solar |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-hot-water-storage-tanks | https://www.sgls.sec.org.sg/categoryinfo.php?cid=58
Singapore Green Labelling Scheme: LEDs | This category establishes criteria for a range of Light Emitting Diode (“LED lighting”), which is used by directly connecting to a commercial power source. | Singapore* | Streetlighting, Non-Directional lamps, Directional Lamps | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2017 | November 2020 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-leds | https://www.sgls.sec.org.sg/categoryinfo.php?cid=45
Singapore Green Labelling Scheme: Photovoltaic Equipment | This category establishes criteria for products for indoor and outdoor use, powered by solar (or light) energy using a rechargeable electrochemical storage system are included within the scope of this category based on environmental, performance, and health parameters. | Singapore* | Small-Solar Powered Electronics | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Solar |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-photovoltaic-equipment | https://www.sgls.sec.org.sg/categoryinfo.php?cid=71
Singapore Green Labelling Scheme: Refrigerators and Freezers | This category establishes criteria for electric household refrigerators (with or without low-temperature compartment), refrigerator-freezer combinations and freezers (chest and upright freezers) used as free-standing, built-under or built-in appliances. | Singapore* | Refrigerators-Freezers | Voluntary | Endorsement Label | Entered into force, Revised | 2012 | 2012 | January 2016 | Electricity |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-refrigerators-and-freezers | https://www.sgls.sec.org.sg/
Singapore Green Labelling Scheme: Solar-Powered Products | The scope of certification under this category includes solar powered products such as watches/clocks, caliper gauges, desktop and pocket calculators, scales for small utilisation, e.g. letter, parcel, bathroom and kitchen scales, titrating devices, toys, solar construction kits, solar training kits, and solar experimental kits. | Singapore* | Small-Solar Powered Electronics, Solar Energy Kits | Voluntary | Endorsement Label | Entered into force, New | 2017 |  | November 2020 | Solar |  | Singapore Environment Council | Energy Efficiency | https://cprc-clasp.ngo/index.php/policies/singapore-green-labelling-scheme-solar-powered-products | https://www.sgls.sec.org.sg/categoryinfo.php?cid=62