## Worksheet
title | Policy Name | Source | Policy Description | Adopted Date | Region | Geography | Changed | Fuel Types | Policy Status | Policy Status Revised Date | Policy Status Updated by CLASP Date | Policy Type | Products Covered | Related Topics | Requirements | Responsible Agency | Scope | Test Method Applied | Permalink
Draft 2025 Energy Code Express Terms | Draft 2025 Energy Code Express Terms | https://efiling.energy.ca.gov/GetDocument.aspx?tn=252915&DocumentContentId=88051 | Heat pump requirements for commercial buildings: "A. Retail and grocery building spaces in Climate Zones 2 through 15. The space-conditioning system shall be a heat pump. B. Retail and grocery building spaces in Climate Zones 1 and 16 with cooling capacity less than 65,000 Btu/hr. The space-conditioning system shall be an air conditioner with furnace. C. Retail and grocery building spaces in Climate Zones 1 and 16 with cooling capacity 65,000 Btu/hr or greater. The space-conditioning system shall be a dual-fuel heat pump. D. School building spaces. For Climate Zones 2 through 15, the space-conditioning system shall be a heat pump. For Climate Zones 1 and 16, the space-conditioning system shall be a dual-fuel heat pump. E. Office, financial institution, and library building spaces in Climate Zones 1 through 15. The spaceconditioning system shall be a heat pump. F. Office, financial institution, and library building spaces in Climate Zone 16 with cooling capacity less than 65,000 Btu/hr. The space-conditioning system shall be an air conditioner with furnace. G. Office, financial institution, and library building spaces in Climate Zone 16 with cooling capacity 65,000 Btu/hr or greater. The space-conditioning system shall be a dual-fuel heat pump. H. Office spaces in warehouses. The space-conditioning system shall be a heat pump in all climate zones. Exception to Section 140.4(a)2: Systems utilizing recovered heat for space heating. " "ii. New or replacement of single zone packaged rooftop systems with a direct expansion cooling with rated cooling capacity less than 65,000 Btu/hr shall meet the applicable requirements in Items a through d below or shall meet the performance compliance requirements of Section 141.0(b)3. a. Retail and grocery buildings: 1. In Climate Zones 3 through 13 and Climate Zone 15 shall have a heat pump or comply with the requirements specified in Table 141.0-E-1. 2. In Climate Zones 2 and 14 shall have an air conditioner with furnace or a heat pump with economizer. 3. In Climate Zone 1 and 16 shall have an air conditioner with furnace. b. School buildings: 1. In Climate Zones 1 through 15 shall have a heat pump or comply with the requirements specified in Table 141.0-E-1. 2. In Climate Zone 16 shall have an air conditioner with furnace. c. Office and financial institution buildings: 1. In Climate Zones 3 through 13 and 15 shall have a heat pump or comply with the requirements specified in Table 141.0-E-1. 2. In Climate Zone 2 and 14 shall have an air conditioner with furnace or a heat pump with economizer. 3. In Climate Zone 1 shall have an air conditioner with furnace or a heat pump. 4. In Climate Zone 16 shall have an air conditioner with furnace. d. Library buildings: 1. In Climate Zones 1, 3 through 15 shall have a heat pump or comply with the requirements specified in Table 141.0-E-1. 2. In Climate Zone 2 shall have an air conditioner with furnace or a heat pump with economizer. 3. In Climate Zone 16 shall have an air conditioner with furnace. Controls requirements for commercial buildings: "(b) Controls for heat pumps with supplementary heaters, for non-residential and multifamily buildings.. Controls for heat pumps with supplementary heaters for single family residential buildings are provided in Section 150.0(h)9. For non-residential and multi-family buildings Hheat pumps with supplementary electric resistance heaters shall have controls: 1. That prevent supplementary heater operation when the heating load can be met by the heat pump alone; and 2. In which the cut-on temperature for compression heating is higher than the cut-on temperature for supplementary heating, and the cut-off temperature for compression heating is higher than the cut-off temperature for supplementary heating. Exception 1 to Section 110.2(b): The controls may allow supplementary heater operation during: A. Defrost; and B. Transient periods such as start-ups and following room thermostat setpoint advance, if the controls provide preferential rate control, intelligent recovery, staging, ramping or another control mechanism designed to preclude the unnecessary operation of supplementary heating. Exception 2 to Section 110.2(b): Room air-conditioner heat pumps." Heat pump requirements for residential buildings: "ii. When an air conditioner is altered or newly installed in an existing dwelling unit, the system shall comply with the following requirements: A. A heat pump as the primary heating source and sized to meet the greater of heating or cooling load. Supplemental heating may be provided by a new or existing gas furnace or by electric resistance; or B. An air conditioner shall meet the following requirements: a. R-8 duct insulation when ducts located in unconditioned space; and b. Measured leakage of the duct system must not exceed 5 percent of the airflow of the system's air handler as confirmed through field verification and diagnostic testing, following the procedures outlined in Reference Residential Appendix Section RA3.1.4.3.1; and c. In every control mode, airflow shall equal to or exceeds 400 CFM per ton of nominal cooling capacity through the return grilles, and the air-handling unit fan efficacy shall be equal to or less than 0.35 W/CFM. These specific airflow rate and fan efficacy requirements in this section need to be verified through field confirmation and diagnostic testing, following the procedures outlined in Reference Residential Appendix RA3.3; and d. Refrigerant charge verification requirements shall meet Section 150.2(b)1Fi; and e. Vented attics shall have insulation installed to achieve a U-factor of 0.020 or insulation installed at the ceiling level shall result in an insulated thermal resistance of R-49 or greater for the insulation alone; and f. Air seal all accessible areas of the ceiling plane between the attic and the conditioned space in accordance with Section 150.2(b)1Jii. Exception 1 to Section 150.2(b)1Fii: Compliance with Section 150.1(c)6 is not required if the addition of the heat pump exceeds the existing main service panel capacity according to the requirements of California Electrical Code Article 220.83 or 220.87 Documentation of electrical load calculations in accordance with Article 220 must be submitted to the Authority Having Jurisdiction for both the heat pump and proposed air conditioner. Exception 2 to Section 150.2(b)1Fii: Compliance with Section 150.1(c)6 is not required if the addition of the heat pump exceeds the existing heating load by 12,000 Btu/h or more. Documentation of heating load calculations in accordance with 150.0(h). " Controls requirements for residential buildings: "7. Supplementary heating control configuration. Heat pumps with supplementary heat, including, but not limited to electric resistance heaters or gas furnace supplementary heating shall comply with the following requirements: A. Lock out supplementary heating above an outdoor air temperature of no greater than 35°F. There are additional thermostat requirements in section 150.0(i)2. B. The installer shall certify on the Certificate of Installation that the control configuration has been tested in accordance with the testing procedure found in the CF2R. C. The controls may allow supplementary heater operation above 35°F only during defrost; or when the user selects emergency operation. Exception 1 to Section 150.0(h)7: Room air-conditioner heat pumps. Exception 2 to Section 150.0(h)7: Buildings in Climate Zone 15. Exception 3 to Section 150.0(h)7: Buildings with a conditioned floor space less than 500 square feet in climate zones 7. " Heat pump requirements for residential multi-family buildings: "3. Dwelling unit space-conditioning systems. A. Heating system type. Space-conditioning systems serving dwelling units shall meet i or ii. Systems that cannot meet the requirements of i or ii, including multi-zone systems and systems using central boilers or chillers, shall comply with the performance requirements of Section 170.1. i. Multifamily buildings three habitable stories or fewer. For Climate Zones 1 through 15, the spaceconditioning system shall be a heat pump. For Climate Zone 16, the space-conditioning system shall be an air conditioner with furnace. Additionally, balanced ventilation systems serving these dwelling units shall meet the applicable requirements of Section 170.2(c)3Bivc. 2025 Building Energy Efficiency Standards Page 15 SECTION 170.2 – PRESCRIPTIVE APPROACH ii. Multifamily buildings four habitable stories or greater. For Climate Zones 2 through 15, the spaceconditioning system shall be a heat pump. For Climate Zones 1 and 16, the space-conditioning system shall be a dual-fuel heat pump. " Also---electric ready requirements "SECTION 160.9 – MANDATORY REQUIREMENTS FOR ELECTRIC READY BUILDINGS (a) General Requirements. Multifamily buildings shall comply with the applicable requirements of subsection 160.9. The building electrical system shall be sized to meet the future electric requirements of the electric ready equipment specified in sections 160.9(a) through (e)." Controls requirements for multi-family residential buildings: "C. Heat pump controls. All heat pumps with supplementary electric resistance heaters shall be installed with controls that comply with Section 110.2(b). " |  | United States of America* | California | Thu, 02/22/2024 - 17:07 | Electricity | Under development |  | February 2024 | Building Code | Heat Pumps, Air Conditioning | AC-to-heat pump | Mandatory | California Energy Commission ( https://www.energy.ca.gov/ ) | This document is a pre-rulemaking draft of the Express Terms for the 2025 update to the California Energy Code (Part 6 of California's Building Standards Code). It contains heat pump and control requirements for commercial and residential buildings in the state of California. |  | https://cprc-clasp.ngo/policies/draft-2025-energy-code-express-terms